{"text_format":"2","workbook":"xls","n_sheets":18,"sheets":["Device Identification ","Instantaneous Measures","Energies and partial Energies","Tariff Control","Energies per Tariff ","Partial Energie per Tariff","Energie per Phase","Instantaneous Measures S2","Energies and Partial Energy S2","Energies per tariff S2","Partial Energy per Tariff S2","Energy per Phase S2","Network Settings","Overflow Events","Reset of Partial Energies","Debug Info","Modbus Configuration","Device Indentification Block"],"not_rendered":{"charts":0,"images":18,"macros":0,"external_links":1,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Device Identification ","index":0,"n_rows":23,"n_cols":17,"rows_kept":23,"cut":false,"hidden":false,"merged":[[3,6,3,16],[6,6,6,16],[9,6,9,16],[10,6,10,16],[18,0,18,4],[0,0,0,16],[1,0,1,5],[12,6,12,16],[13,6,13,16],[14,6,14,16],[5,6,5,16]],"flags":["formulas_cached_only"]}
["Device Identification "]
["Product reference",{"$nulls":6},"ECR180D\nECR181D","ECA180D\nECA181D","ECR380D                ECR381D","ECA380D                ECA381D","ECR310D                ECR311D","ECA310D                ECA311D","ECR300C                ECR301C","ECA300C                ECA301C","ECR180T","ECA180T"]
["Description","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80 Modbus","1P_80 Agardio","3P_80 Modbus","3P_80 Agardio","3P_125 Modbus","3P_125 Agardio","3P_CT Modbus","3P_CT Agardio","3P_1P80 Modbus","3P_1P80 Agardio"]
["Vendor Name",4096,1000,16,"STRING","H'03'","“Hager”"]
["Product Code",4112,1010,16,"STRING (1)","H'03'","ECR140D","ECR180D","ECA180D","ECR380D                ECR381D","ECA380D                ECA381D","ECR310D                ECR311D","ECA310D                ECA311D","ECR300C                ECR301C","ECA300C                ECA301C","ECR180T","ECA180T"]
["SW version",4128,1020,2,"(2)","H'03'","0x02030000 (in this example, Firmware Version = 2.3.0) "]
["Vendor URL",4130,1022,16,"STRING","H'03'","“http://www.hager.com” "]
["Product Name",4146,1032,16,"STRING","H'03'","1P_40","1P_80 Modbus","1P_80 Agardio","3P_80 Modbus","3P_80 Agardio","3P_125 Modbus","3P_125 Aagrdio","3P_CT Modbus","3P_CT Agardio","3P_1P80 Modbus","3P_1P80 Agardio"]
["Model Name",4162,1042,16,"STRING","H'03'","“MODBUS Screw MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw”","“AGARDIO RJ45”"]
["User Application Name",4178,1052,16,"STRING","H'03'","\"APL\""]
["HW Version",4194,1062,2,"(2)","H'03'","0x04010000 (in this example, Hardware Version = 4.1.0)"]
["Product code (Serial number)",4196,1064,16,"(3)","H'03'","Example: 0318440021 : Ref.Id.=03 for ECR140D Year=2018 Week=44th Progr.N.=0021","Example:0618440021 : Ref.Id.=06 for ECR180D Year=2018 Week=44th Progr.N.=0021","Example: 0718440021 : Ref.Id.=07 for ECA180D Year=2018 Week=44th Progr.N.=0021","Example: 3418440021 : Ref.Id.=34 for ECR380D Year=2018 Week=44th Progr.N.=0021","Example: 3618440021 : Ref.Id.=36 for ECA380D Year=2018 Week=44th Progr.N.=0021","Example: 4218440021 : Ref.Id.=42 for ECR310D Year=2018 Week=44th Progr.N.=0021","Example: 4418440021 : Ref.Id.=44 for ECA310D Year=2018 Week=44th Progr.N.=0021","Example: 5018440021 : Ref.Id.=50 for ECR300D Year=2018 Week=44th Progr.N.=0021","Example: 5218440021 : Ref.Id.=52 for ECA300D Year=2018 Week=44th Progr.N.=0021","Example: 2218440021 : Ref.Id.=22 for ECR180T Year=2018 Week=44th Progr.N.=0021","Example: 2318440021 : Ref.Id.=23 for ECA180T Year=2018 Week=44th Progr.N.=0021"]
["Product code (Site Code)",4212,1074,2,"STRING","H'03'","\"I\" (\"I\" indicates Italy)"]
["Production Date (Day of the Year)",4214,1076,1,"U16","H'03'","213 (example, means 213th day of the Year)"]
["Production Date (Year)",4215,1077,1,"U16","H'03'","2018 (example)"]
[]
[]
["(1) Chars sequence\nIn case of Swiss market\n"]
["(2) 3 levels version For example: 1.2.3 is coded 0x01020300\n\n\n",{"$nulls":5},21]
["In Strings data type values, chars are in  sequence, with first char in MSByte. For example, “Hager “ in Vendor Name  is in the following sequence:"]
["Word 1: ‘H’ in Msbyte, ‘a’ in lsbyte Word2: ‘g’ in MSbyte, ‘e’ in lsbyte Word 3: ‘r’ in MSbyte, ‘/0‘ in lsbyte"]
["the other words from 4 to 16 are full of blanks (\\0, chr$(0))"]
["Strings Swiss(*): these product codes are dedicated to those versions that do not show Reactive Energies on the display (Swiss market)"]

{"sheet":"Instantaneous Measures","index":1,"n_rows":40,"n_cols":14,"rows_kept":40,"cut":false,"hidden":false,"merged":[[1,0,1,7],[39,0,39,5],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Instantaneous Measures"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80 (*)"]
["V(L1-N)","V",0.01,45056,"B000",1,"U16","H'03'","9200…27600","9200…27600","9200…27600","9200…27600","9200…27600","9200…27600"]
["V(L2-N)","V",0.01,45057,"B001",1,"U16","H'03'","0xFFFF","0xFFFF","9200…27600","9200…27600","9200…27600","9200…27600"]
["V(L3-N)","V",0.01,45058,"B002",1,"U16","H'03'","0xFFFF","0xFFFF","9200…27600","9200…27600","9200…27600","9200…27600"]
["V(L1-L2)","V",0.01,45059,"B003",1,"U16","H'03'","0xFFFF","0xFFFF","16000…48000","16000…48000","16000…48000","0xFFFF"]
["V(L2-L3)","V",0.01,45060,"B004",1,"U16","H'03'","0xFFFF","0xFFFF","16000…48000","16000…48000","16000…48000","0xFFFF"]
["V(L3-L1)","V",0.01,45061,"B005",1,"U16","H'03'","0xFFFF","0xFFFF","16000…48000","16000…48000","16000…48000","0xFFFF"]
["F","Hz",0.01,45062,"B006",1,"U16","H'03'","4500…6500","4500…6500","4500…6500","4500…6500","4500…6500","4500…6500"]
["Not Used","Hz",0.01,45063,"B007",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0xFFFF"]
["Not Used","Hz",0.01,45064,"B008",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0xFFFF"]
["I(L1)","mA",1,45065,"B009",2,"U32","H'03'","0…40000","0…80000","0…80000","0…125000","0…7200000","0…80000"]
["I(L2)","mA",1,45067,"B00B",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…80000","0…125000","0…7200000","0…80000"]
["I(L3)","mA",1,45069,"B00D",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…80000","0…125000","0…7200000","0…80000"]
["I(Neutral)","mA",1,45071,"B00F",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…80000","0…125000","0…7200000","0xFFFFFFFF"]
["P(ΣL)","±KW",0.01,45073,"B011",2,"S32","H'03'","-1104…+1104","-2208…+2208","-6624…+6624","-10350…+10350","-596160…+596160","0x7FFFFFFF"]
["Q(ΣL)","±kvar",0.01,45075,"B013",2,"S32","H'03'","-1104…+1104","-2208…+2208","-6624…+6624","-10350…+10350","-596160…+596160","0x7FFFFFFF "]
["S(ΣL)","KvA",0.01,45077,"B015",2,"U32","H'03'","0…1104","0…2208","0…6624","0…10350","0…596160","0xFFFFFFFF"]
["PF(ΣL) IEC (§)",null,0.001,45079,"B017",1,"S16","H'03'","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","0x7FFF"]
["PF(ΣL) IEEE (§)",null,0.001,45080,"B018",1,"S16","H'03'","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","0x7FFF"]
["P(L1)","±KW",0.01,45081,"B019",2,"S32","H'03'","-1104…+1104","-2208…+2208","-2208…+2208","-3450…+3450","-198720…+198720","-2208…+2208"]
["P(L2)","±KW",0.01,45083,"B01B",2,"S32","H'03'","0x7FFFFFFF","0x7FFFFFFF","-2208…+2208","-3450…+3450","-198720…+198720","-2208…+2208"]
["P(L3)","±KW",0.01,45085,"B01D",2,"S32","H'03'","0x7FFFFFFF","0x7FFFFFFF","-2208…+2208","-3450…+3450","-198720…+198720","-2208…+2208"]
["Q(L1)","±kvar",0.01,45087,"B01F",2,"S32","H'03'","-1104…+1104","-2208…+2208","-2208…+2208","-3450…+3450","-198720…+198720","-2208…+2208"]
["Q(L2)","±kvar",0.01,45089,"B021",2,"S32","H'03'","0x7FFFFFFF","0x7FFFFFFF","-2208…+2208","-3450…+3450","-198720…+198720","-2208…+2208"]
["Q(L3)","±kvar",0.01,45091,"B023",2,"S32","H'03'","0x7FFFFFFF","0x7FFFFFFF","-2208…+2208","-3450…+3450","-198720…+198720","-2208…+2208"]
["S(L1)","KvA",0.01,45093,"B025",2,"U32","H'03'","0…1104","0…2208","0…2208","0…3450","0…198720","0…2208"]
["S(L2)","KvA",0.01,45095,"B027",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…2208","0…3450","0…198720","0…2208"]
["S(L3)","KvA",0.01,45097,"B029",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…2208","0…3450","0…198720","0…2208"]
["PF(L1) IEC (§)",null,0.001,45099,"B02B",1,"S16","H'03'","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000"]
["PF(L2) IEC (§)",null,0.001,45100,"B02C",1,"S16","H'03'","0x7FFF","0x7FFF","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000"]
["PF(L3) IEC (§)",null,0.001,45101,"B02D",1,"S16","H'03'","0x7FFF","0x7FFF","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000"]
["PF(L1) IEEE (§)",null,0.001,45102,"B02E",1,"S16","H'03'","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","-1000…+1000","0x7FFF"]
["PF(L2) IEEE (§)",null,0.001,45103,"B02F",1,"S16","H'03'","0x7FFF","0x7FFF","-1000…+1000","-1000…+1000","-1000…+1000","0x7FFF"]
["PF(L3) IEEE (§)",null,0.001,45104,"B030",1,"S16","H'03'","0x7FFF","0x7FFF","-1000…+1000","-1000…+1000","-1000…+1000","0x7FFF"]
[]
[]
["(*) in 3ple_1P_80A L1 means Meter 1, L2 means  Meter2 and L3 means Meter3"]
["(§) In case no power is flowing (Ln or ΣL), Power Factor is = +1000."]

{"sheet":"Energies and partial Energies","index":2,"n_rows":22,"n_cols":14,"rows_kept":22,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Energies and partial Energies"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Ea+ (ΣT)","kWh",1,45152,"B060",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ (ΣT)","kvarh",1,45154,"B062",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- (ΣT)","kWh",1,45156,"B064",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- (ΣT)","kvarh",1,45158,"B066",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ (ΣT)","kWh",1,45160,"B068",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- (ΣT)","kWh",1,45162,"B06A",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
[]
["Ea+ (M1)(ΣT)","kWh",1,45184,"B080",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ (M2)(ΣT)","kWh",1,45186,"B082",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ (M3)(ΣT)","kWh",1,45188,"B084",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- (M1)(ΣT)","kWh",1,45190,"B086",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- (M2)(ΣT)","kWh",1,45192,"B088",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- (M3)(ΣT)","kWh",1,45194,"B08A",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ (M1)(ΣT)","kWh",1,45196,"B08C",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ (M2)(ΣT)","kWh",1,45198,"B08E",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ (M3)(ΣT)","kWh",1,45200,"B090",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- (M1)(ΣT)","kWh",1,45202,"B092",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- (M2)(ΣT)","kWh",1,45204,"B094",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- (M3)(ΣT)","kWh",1,45206,"B096",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]

{"sheet":"Tariff Control","index":3,"n_rows":8,"n_cols":13,"rows_kept":8,"cut":false,"hidden":false,"merged":[[7,7,7,12],[0,0,0,12],[1,0,1,6],[3,7,3,12],[4,7,4,12],[5,7,5,12],[6,7,6,12]],"flags":["formulas_cached_only"]}
["Tariff Control"]
["Product reference",{"$nulls":6},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Number of available Tariffs = 8 (or 4)",null,45232,"B0B0",1,"U16","H'03'","Always = 8 (4 in 3ple_1P_80A)"]
["Active Tariff on the product, regarding the Tariff Mode and physical input OR Modbus Tariff",null,45233,"B0B1",1,"U16","H'03'","1…8 (1…4 in 3ple_1P_80A)"]
["Physical Input Driven Tariff ",null,45234,"B0B2",1,"U16","H'03'","1…2 (0xFFFF in 1P_40 and 1P_80 Agardio, because  they have no physical tariff digital input)"]
["Tariff Mode: 0 or 1 (read only, can only be changed through HMI)",null,45235,"B0B3",1,"U16","H'03'","0:  tariff is HW driven (active tariff=Physical tariff) 1:  tariff is  Modbus driven (tariff by writing Set Tariff) (the tariff mode is defined by means of keyboard and display, except 1P_40 40 because it has no physical tariff digital input, hence Tariff_mode is always = 1)"]
["Set Tariff (writable)  (always read as 0)",null,45236,"B0B4",1,"U16","H'06'","1…8 (1…4 in 3ple_1P_80A) writable (always read as 0)"]

{"sheet":"Energies per Tariff ","index":4,"n_rows":60,"n_cols":14,"rows_kept":60,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Energies per Tariff "]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Ea+ [T1]","kWh",1,45248,"B0C0",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T2]","kWh",1,45250,"B0C2",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T3]","kWh",1,45252,"B0C4",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T4]","kWh",1,45254,"B0C6",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T5]","kWh",1,45256,"B0C8",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T6]","kWh",1,45258,"B0CA",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T7]","kWh",1,45260,"B0CC",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+ [T8]","kWh",1,45262,"B0CE",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T1]","kWh",1,45264,"B0D0",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T2]","kWh",1,45266,"B0D2",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T3]","kWh",1,45268,"B0D4",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T4]","kWh",1,45270,"B0D6",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T5]","kWh",1,45272,"B0D8",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T6]","kWh",1,45274,"B0DA",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T7]","kWh",1,45276,"B0DC",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea- [T8]","kWh",1,45278,"B0DE",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T1]","kvarh",1,45280,"B0E0",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T2]","kvarh",1,45282,"B0E2",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T3]","kvarh",1,45284,"B0E4",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T4]","kvarh",1,45286,"B0E6",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T5]","kvarh",1,45288,"B0E8",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T6]","kvarh",1,45290,"B0EA",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T7]","kvarh",1,45292,"B0EC",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+ [T8]","kvarh",1,45294,"B0EE",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T1]","kvarh",1,45296,"B0F0",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T2]","kvarh",1,45298,"B0F2",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T3]","kvarh",1,45300,"B0F4",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T4]","kvarh",1,45302,"B0F6",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T5]","kvarh",1,45304,"B0F8",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T6]","kvarh",1,45306,"B0FA",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T7]","kvarh",1,45308,"B0FC",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er- [T8]","kvarh",1,45310,"B0FE",2,"U32","H'03'","0…99,999","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
[]
["Ea+ [M1] [T1]","kWh",1,45488,"B1B0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M1] [T2]","kWh",1,45490,"B1B2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M1] [T3]","kWh",1,45492,"B1B4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M1] [T4]","kWh",1,45494,"B1B6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M1] [T1]","kWh",1,45496,"B1B8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M1] [T2]","kWh",1,45498,"B1BA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M1] [T3]","kWh",1,45500,"B1BC",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M1] [T4]","kWh",1,45502,"B1BE",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M2] [T1]","kWh",1,45504,"B1C0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M2] [T2]","kWh",1,45506,"B1C2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M2] [T3]","kWh",1,45508,"B1C4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M2] [T4]","kWh",1,45510,"B1C6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M2] [T1]","kWh",1,45512,"B1C8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M2] [T2]","kWh",1,45514,"B1CA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M2] [T3]","kWh",1,45516,"B1CC",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M2] [T4]","kWh",1,45518,"B1CE",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M3] [T1]","kWh",1,45520,"B1D0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M3] [T2]","kWh",1,45522,"B1D2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M3] [T3]","kWh",1,45524,"B1D4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea+ [M3] [T4]","kWh",1,45526,"B1D6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M3] [T1]","kWh",1,45528,"B1D8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M3] [T2]","kWh",1,45530,"B1DA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M3] [T3]","kWh",1,45532,"B1DC",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["Ea- [M3] [T4]","kWh",1,45534,"B1DE",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]

{"sheet":"Partial Energie per Tariff","index":5,"n_rows":44,"n_cols":14,"rows_kept":44,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Partial Energie per Tariff"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["P_Ea+ [T1]","kWh",1,45376,"B140",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T2]","kWh",1,45378,"B142",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T3]","kWh",1,45380,"B144",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T4]","kWh",1,45382,"B146",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T5]","kWh",1,45384,"B148",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T6]","kWh",1,45386,"B14A",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T7]","kWh",1,45388,"B14C",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea+ [T8]","kWh",1,45390,"B14E",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T1]","kWh",1,45392,"B150",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T2]","kWh",1,45394,"B152",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T3]","kWh",1,45396,"B154",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T4]","kWh",1,45398,"B156",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T5]","kWh",1,45400,"B158",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T6]","kWh",1,45402,"B15A",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T7]","kWh",1,45404,"B15C",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["P_Ea- [T8]","kWh",1,45406,"B15E",2,"U32","H'03'","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
[]
["P_Ea+ [M1] [T1]","kWh",1,45584,"B210",2,"U33","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M1] [T2]","kWh",1,45586,"B212",2,"U34","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M1] [T3]","kWh",1,45588,"B214",2,"U35","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M1] [T4]","kWh",1,45590,"B216",2,"U36","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M1] [T1]","kWh",1,45592,"B218",2,"U37","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M1] [T2]","kWh",1,45594,"B21A",2,"U38","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M1] [T3]","kWh",1,45596,"B21C",2,"U39","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M1] [T4]","kWh",1,45598,"B21E",2,"U40","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M2] [T1]","kWh",1,45600,"B220",2,"U41","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M2] [T2]","kWh",1,45602,"B222",2,"U42","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M2] [T3]","kWh",1,45604,"B224",2,"U43","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M2] [T4]","kWh",1,45606,"B226",2,"U44","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M2] [T1]","kWh",1,45608,"B228",2,"U45","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M2] [T2]","kWh",1,45610,"B22A",2,"U46","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M2] [T3]","kWh",1,45612,"B22C",2,"U47","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M2] [T4]","kWh",1,45614,"B22E",2,"U48","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M3] [T1]","kWh",1,45616,"B230",2,"U49","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M3] [T2]","kWh",1,45618,"B232",2,"U50","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M3] [T3]","kWh",1,45620,"B234",2,"U51","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea+ [M3] [T4]","kWh",1,45622,"B236",2,"U52","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M3] [T1]","kWh",1,45624,"B238",2,"U53","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M3] [T2]","kWh",1,45626,"B23A",2,"U54","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M3] [T3]","kWh",1,45628,"B23C",2,"U55","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]
["P_Ea- [M3] [T4]","kWh",1,45630,"B23E",2,"U56","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999"]

{"sheet":"Energie per Phase","index":6,"n_rows":15,"n_cols":14,"rows_kept":15,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Energie per Phase"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Ea+[L1]","kWh",1,45440,"B180",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+[L2]","kWh",1,45442,"B182",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea+[L3]","kWh",1,45444,"B184",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea-[L1]","kWh",1,45446,"B186",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea-[L2]","kWh",1,45448,"B188",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Ea-[L3]","kWh",1,45450,"B18A",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+[L1]","kvarh",1,45452,"B18C",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+[L2]","kvarh",1,45454,"B18E",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er+[L3]","kvarh",1,45456,"B190",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er-[L1]","kvarh",1,45458,"B192",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er-[L2]","kvarh",1,45460,"B194",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]
["Er-[L3]","kvarh",1,45462,"B196",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0…9,999,999","0…9,999,999","0…99,999,999","0xFFFFFFFF"]

{"sheet":"Instantaneous Measures S2","index":7,"n_rows":34,"n_cols":14,"rows_kept":34,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Instantaneous Measures Secondary"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["V(L1-N)","V",0.01,45680,"B270",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","9200…27600","0xFFFF"]
["V(L2-N)","V",0.01,45681,"B271",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","9200…27600","0xFFFF"]
["V(L3-N)","V",0.01,45682,"B272",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","9200…27600","0xFFFF"]
["V(L1-L2)","V",0.01,45683,"B273",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","16000…48000","0xFFFF"]
["V(L2-L3)","V",0.01,45684,"B274",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","16000…48000","0xFFFF"]
["V(L3-L1)","V",0.01,45685,"B275",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","16000…48000","0xFFFF"]
["F","Hz",0.01,45686,"B276",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","4500…6500","0xFFFF"]
["I(L1)","mA",1,45687,"B277",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…6000","0xFFFF"]
["I(L2)","mA",1,45688,"B278",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…6000","0xFFFF"]
["I(L3)","mA",1,45689,"B279",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…6000","0xFFFF"]
["I(Neutral)","mA",1,45690,"B27A",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…6000","0xFFFF"]
["P(ΣL)","±W",1,45691,"B27B",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-4968…+4968","0x7FFF"]
["Q(ΣL)","±var",1,45692,"B27C",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-4968…+4968","0x7FFF"]
["S(ΣL)","VA",1,45693,"B27D",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…4968","0xFFFF"]
["PF(ΣL) IEC (§)",null,0.001,45694,"B27E",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["PF(ΣL) IEEE (§)",null,0.001,45695,"B27F",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["P(L1)","±W",1,45696,"B280",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1656…+1656","0x7FFF"]
["P(L2)","±W",1,45697,"B281",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1656…+1656","0x7FFF"]
["P(L3)","±W",1,45698,"B282",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1656…+1656","0x7FFF"]
["Q(L1)","±var",1,45699,"B283",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1656…+1656","0x7FFF"]
["Q(L2)","±var",1,45700,"B284",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1656…+1656","0x7FFF"]
["Q(L3)","±var",1,45701,"B285",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1656…+1656","0x7FFF"]
["S(L1)","VA",1,45702,"B286",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…1656","0xFFFF"]
["S(L2)","VA",1,45703,"B287",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…1656","0xFFFF"]
["S(L3)","VA",1,45704,"B288",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","0…1656","0xFFFF"]
["PF(L1) IEC (§)",null,0.001,45705,"B289",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["PF(L2) IEC (§)",null,0.001,45706,"B28A",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["PF(L3) IEC (§)",null,0.001,45707,"B28B",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["PF(L1) IEEE (§)",null,0.001,45708,"B28C",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["PF(L2) IEEE (§)",null,0.001,45709,"B28D",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]
["PF(L3) IEEE (§)",null,0.001,45710,"B28E",1,"U16","H'03'","0x7FFF","0x7FFF","0x7FFF","0x7FFF","-1000…+1000","0x7FFF"]

{"sheet":"Energies and Partial Energy S2","index":8,"n_rows":9,"n_cols":14,"rows_kept":9,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Energies and Partial Energy Secondary"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Ea+ (ΣT)","kWh",0.01,45744,"B2B0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ (ΣT)","kvarh",0.01,45746,"B2B2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- (ΣT)","kWh",0.01,45748,"B2B4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- (ΣT)","kvarh",0.01,45750,"B2B6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ (ΣT)","kWh",0.01,45752,"B2B8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- (ΣT)","kWh",0.01,45754,"B2BA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]

{"sheet":"Energies per tariff S2","index":9,"n_rows":35,"n_cols":14,"rows_kept":35,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Energies per tariff Secondary"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Ea+ [T1]","kWh",0.01,45776,"B2D0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T2]","kWh",0.01,45778,"B2D2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T3]","kWh",0.01,45780,"B2D4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T4]","kWh",0.01,45782,"B2D6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T5]","kWh",0.01,45784,"B2D8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T6]","kWh",0.01,45786,"B2DA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T7]","kWh",0.01,45788,"B2DC",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [T8]","kWh",0.01,45790,"B2DE",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T1]","kWh",0.01,45792,"B2E0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T2]","kWh",0.01,45794,"B2E2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T3]","kWh",0.01,45796,"B2E4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T4]","kWh",0.01,45798,"B2E6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T5]","kWh",0.01,45800,"B2E8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T6]","kWh",0.01,45802,"B2EA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T7]","kWh",0.01,45804,"B2EC",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [T8]","kWh",0.01,45806,"B2EE",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T1]","kvarh",0.01,45808,"B2F0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T2]","kvarh",0.01,45810,"B2F2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T3]","kvarh",0.01,45812,"B2F4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T4]","kvarh",0.01,45814,"B2F6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T5]","kvarh",0.01,45816,"B2F8",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T6]","kvarh",0.01,45818,"B2FA",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T7]","kvarh",0.01,45820,"B2FC",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [T8]","kvarh",0.01,45822,"B2FE",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T1]","kvarh",0.01,45824,"B300",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T2]","kvarh",0.01,45826,"B302",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T3]","kvarh",0.01,45828,"B304",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T4]","kvarh",0.01,45830,"B306",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T5]","kvarh",0.01,45832,"B308",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T6]","kvarh",0.01,45834,"B30A",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T7]","kvarh",0.01,45836,"B30C",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [T8]","kvarh",0.01,45838,"B30E",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]

{"sheet":"Partial Energy per Tariff S2","index":10,"n_rows":19,"n_cols":14,"rows_kept":19,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Partial Energy per Tariff Secondary"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["P_Ea+ [T1]","kWh",0.01,45904,"B350",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T2]","kWh",0.01,45906,"B352",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T3]","kWh",0.01,45908,"B354",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T4]","kWh",0.01,45910,"B356",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T5]","kWh",0.01,45912,"B358",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T6]","kWh",0.01,45914,"B35A",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T7]","kWh",0.01,45916,"B35C",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea+ [T8]","kWh",0.01,45918,"B35E",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T1]","kWh",0.01,45920,"B360",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T2]","kWh",0.01,45922,"B362",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T3]","kWh",0.01,45924,"B364",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T4]","kWh",0.01,45926,"B366",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T5]","kWh",0.01,45928,"B368",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T6]","kWh",0.01,45930,"B36A",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T7]","kWh",0.01,45932,"B36C",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["P_Ea- [T8]","kWh",0.01,45934,"B36E",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]

{"sheet":"Energy per Phase S2","index":11,"n_rows":15,"n_cols":14,"rows_kept":15,"cut":false,"hidden":false,"merged":[[1,0,1,7],[0,0,0,13]],"flags":["formulas_cached_only"]}
["Energy per Phase Secondary"]
["Product reference",{"$nulls":7},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Resolution","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Ea+ [L1]","kWh",0.01,45968,"B390",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [L2]","kWh",0.01,45970,"B392",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea+ [L3]","kWh",0.01,45972,"B394",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [L1]","kWh",0.01,45974,"B396",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [L2]","kWh",0.01,45976,"B398",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Ea- [L3]","kWh",0.01,45978,"B39A",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [L1]","kvarh",0.01,45980,"B39C",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [L2]","kvarh",0.01,45982,"B39E",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er+ [L3]","kvarh",0.01,45984,"B3A0",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [L1]","kvarh",0.01,45986,"B3A2",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [L2]","kvarh",0.01,45988,"B3A4",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]
["Er- [L3]","kvarh",0.01,45990,"B3A6",2,"U32","H'03'","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0xFFFFFFFF","0…8,333,333","0xFFFFFFFF"]

{"sheet":"Network Settings","index":12,"n_rows":7,"n_cols":13,"rows_kept":7,"cut":false,"hidden":false,"merged":[[1,0,1,6],[0,0,0,12]],"flags":["formulas_cached_only"]}
["Network Settings"]
["Product reference",{"$nulls":6},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Network Type","enum",49152,"C000",1,"U16","H'03'","1 : 1BL","1 : 1BL","4 : 4NBL","4 : 4NBL","4 : 4NBL","1 : 1BL"]
["CT secondary","A",49153,"C001",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","1 or 5","0xFFFF"]
["CT primary","A",49154,"C002",1,"U16","H'03'","0xFFFF","0xFFFF","0xFFFF","0xFFFF","1…1200 Or 5…6000","0xFFFF"]
["MID Certified","enum",49155,"C003",1,"U16","H'03'","Always 1 =MID","Always 1 =MID","Always 1 =MID","Always 1 =MID","Always 1 =MID","Always 0=no MID"]

{"sheet":"Overflow Events","index":13,"n_rows":17,"n_cols":13,"rows_kept":17,"cut":false,"hidden":false,"merged":[[1,0,1,6],[10,0,10,6],[0,0,0,12]],"flags":["formulas_cached_only"]}
["Overflow Events"]
["Product reference",{"$nulls":6},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT"]
["Overflow value","kWh/kvarh",49168,"C010",2,"U32","H'03'",100,"10,000,000","10,000,000","10,000,000",83.333]
["Number of Overflow Events for Ea+",null,49170,"C012",1,"U16","H'03'","0…255","0…255","0…255","0…255","0…255"]
["Number of Overflow Events for Er+",null,49171,"C013",1,"U16","H'03'","0…255","0…255","0…255","0…255","0…255"]
["Number of Overflow Events for Ea-",null,49172,"C014",1,"U16","H'03'","0…255","0…255","0…255","0…255","0…255"]
["Number of Overflow Events for Er-",null,49173,"C015",1,"U16","H'03'","0…255","0…255","0…255","0…255","0…255"]
[]
[]
["Product reference",{"$nulls":11},"ECR180T"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function",{"$nulls":5},"3P_1P80"]
["Overflow value","kWh/kvarh",49168,"C010",2,"U32","H'03'",{"$nulls":5},"10,000,000"]
["In the Most Significant byte:  Number of Overflow Events for Ea+ [Meter1]               In the Least Significant byte:  Number of Overflow Events for Ea- [Meter1]",null,49170,"C012",1,"U16","H'03'",{"$nulls":5},"MS byte 0…255        LS byte 0…255"]
["In the Most Significant byte:  Number of Overflow Events for Ea+ [Meter2]               In the Least Significant byte:  Number of Overflow Events for Ea- [Meter2]",null,49171,"C013",1,"U16","H'03'",{"$nulls":5},"MS byte 0…255        LS byte 0…255"]
["In the Most Significant byte:  Number of Overflow Events for Ea+ [Meter3]               In the Least Significant byte:  Number of Overflow Events for Ea- [Meter3]",null,49172,"C014",1,"U16","H'03'",{"$nulls":5},"MS byte 0…255        LS byte 0…255"]
[null,null,49173,"C015",1,"U16",{"$nulls":6},"0xFFFF"]

{"sheet":"Reset of Partial Energies","index":14,"n_rows":23,"n_cols":13,"rows_kept":23,"cut":false,"hidden":false,"merged":[[1,0,1,6],[0,0,0,12]],"flags":["formulas_cached_only"]}
["Reset of Partial Energies"]
["Product reference",{"$nulls":6},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Bit 0 clear all the Partial Registers of Tariff 1",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0/1"]
["Bit 1 clear all the Partial Registers of Tariff 2",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0/1"]
["Bit 2 clear all the Partial Registers of Tariff 3",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0/1"]
["Bit 3 clear all the Partial Registers of Tariff 4",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0/1"]
["Bit 4 clear all the Partial Registers of Tariff 5",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","-"]
["Bit 5 clear all the Partial Registers of Tariff 6",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","-"]
["Bit 6 clear all the Partial Registers of Tariff 7",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","-"]
["Bit 7 clear all the Partial Registers of Tariff 8",null,49184,"C020",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","-"]
["Bit 0 clear the Partial Registers of Tariff 1 of Meter1",null,49185,"C021",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 1 clear the Partial Registers of Tariff 2 of Meter1",null,49185,"C021",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 2 clear the Partial Registers of Tariff 3 of Meter1",null,49185,"C021",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 3 clear the Partial Registers of Tariff 4 of Meter1",null,49185,"C021",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 0 clear the Partial Registers of Tariff 1 of Meter2",null,49186,"C022",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 1 clear the Partial Registers of Tariff 2 of Meter2",null,49186,"C022",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 2 clear the Partial Registers of Tariff 3 of Meter2",null,49186,"C022",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 3 clear the Partial Registers of Tariff 4 of Meter2",null,49186,"C022",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 0 clear the Partial Registers of Tariff 1 of Meter3",null,49187,"C023",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 1 clear the Partial Registers of Tariff 2 of Meter3",null,49187,"C023",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 2 clear the Partial Registers of Tariff 3 of Meter3",null,49187,"C023",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]
["Bit 3 clear the Partial Registers of Tariff 4 of Meter3",null,49187,"C023",null,"U16","H'03', H'06'","0xFFFF","0/1","0/1","0/1","0/1","0xFFFF"]

{"sheet":"Debug Info","index":15,"n_rows":5,"n_cols":13,"rows_kept":5,"cut":false,"hidden":false,"merged":[[1,0,1,6],[0,0,0,12]],"flags":["formulas_cached_only"]}
["Debug Info"]
["Product reference",{"$nulls":6},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Number of device switch-on since its production",null,49200,"C030",1,"U16","H'03'","1…999","1…999","1…999","1…999","1…999","1…999"]
["Number of Buttons pushes ",null,49201,"C031",1,"U16","H'03'","1…9999","1…9999","1…9999","1…9999","1…9999","1…9999"]

{"sheet":"Modbus Configuration","index":16,"n_rows":17,"n_cols":13,"rows_kept":17,"cut":false,"hidden":false,"merged":[[1,0,1,6],[0,0,0,12]],"flags":["formulas_cached_only"]}
["Modbus Configuration"]
["Product reference",{"$nulls":6},"ECR140D","ECR180D ECR181D   ECA180D ECA181D","ECR380D ECR381D ECA380D ECA381D","ECR310D ECR311D    ECA310D ECA311D","ECR300C ECR301C    ECA300C ECA301C","ECR180T"]
["Description","Unit","Address DEC","Address HEX","Lengh (word)","Data Type","Function","1P_40","1P_80","3P_80","3P_125","3P_CT","3P_1P80"]
["Modbus Address (writable)",null,49216,"C040",1,"U16","H'03'","1…999","1…999","1…999","1…999","1…999","1…999"]
["Modbus Baud Rate, Modbus Parity & Stop Bits (writable)",null,49217,"C041",1,"U16","H'03'"]
[]
["MSbyte = Baud Rate","Lsbyte = Parity"]
["0x00 : 1200","0x00 = No Parity, 1 Stop Bit"]
["0x01 : 2400","0x01 = No Parity, 2 Stop Bits"]
["0x02 : 4800","0x02 = Odd Parity, 1 Stop Bit"]
["0x03 : 9600","0x03 = Odd Parity, 2 Stop Bits"]
["0x04 : 19200","0x04 = Even Parity, 1 Stop Bit"]
["0x05 : 38400","0x05 = Even Parity, 2 Stop Bits"]
[]
["Examples: "]
["0x0401 ß> 19200 baud, No Parity, 2 Stop Bits"]
["0x0004 ß> 1200 baud, Even Parity, 1 Stop Bit"]

{"sheet":"Device Indentification Block","index":17,"n_rows":23,"n_cols":15,"rows_kept":23,"cut":false,"hidden":false,"merged":[[10,4,10,14],[12,4,12,14],[13,4,13,14],[14,4,14,14],[11,4,11,14],[0,0,0,14],[1,0,1,3],[3,4,3,14],[5,4,5,14],[6,4,6,14],[9,4,9,14]],"flags":["formulas_cached_only"]}
["Device Identification"]
["Product reference",{"$nulls":4},"ECR180D\nECR181D","ECA180D\nECA181D","ECR380D                ECR381D","ECA380D                ECA381D","ECR310D                ECR311D","ECA310D                ECA311D","ECR300C                ECR301C","ECA300C                ECA301C","ECR180T","ECA180T"]
["Description","Object ID","Data Type","Function","1P_40","1P_80 Modbus","1P_80 Agardio","3P_80 Modbus","3P_80 Agardio","3P_125 Modbus","3P_125 Agardio","3P_CT Modbus","3P_CT Agardio","3P_1P80 Modbus","3P_1P80 Agardio"]
["Vendor Name","0x00","ASCII","H'2B', H0E","“Hager”"]
["Product Code In case of Swiss Mkt","0x01","ASCII","H'2B', H0E","ECR140D","ECR180D","ECA180D","ECR380D                ECR381D","ECA380D                ECA381D","ECR310D                ECR311D","ECA310D                ECA311D","ECR300C                ECR301C","ECA300C                ECA301C","ECR180T","ECA180T"]
["Product Version","0x02","ASCII","H'2B', H0E","0x02030000 (in this example, Firmware Version = 2.3.0) "]
["Vendor URL","0x03","ASCII","H'2B', H0E","“http://www.hager.com” "]
["Product Name","0x04","ASCII","H'2B', H0E","1P_40","1P_80 Modbus","1P_80 Agardio","3P_80 Modbus","3P_80 Agardio","3P_125 Modbus","3P_125 Aagrdio","3P_CT Modbus","3P_CT Agardio","3P_1P80 Modbus","3P_1P80 Agardio"]
["Model Name","0x05","ASCII","H'2B', H0E","“MODBUS Screw MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw MID”","“AGARDIO RJ45 MID”","“MODBUS Screw”","“AGARDIO RJ45”"]
["User Application Name","0x06","ASCII","H'2B', H0E","\"APL\""]
["Serial","0x80","ASCII","H'2B', H0E","“0218230020”         (example)"]
["Production Date","0x81","ASCII","H'2B', H0E","“ddd/YYYY”                               (example = “143/2018”)"]
["Hardware Version","0x82","ASCII","H'2B', H0E","“1.4.0” (example)"]
[]
["Applicable Functions:  Read_Device_Identification (0x2B/0x0E)"]
[]
["User Blocks"]
[]
["Applicable Functions:  User-Defined Functions (0x43/0x01, 0x43/0x02, 0x43/0x03)"]
["Refer to “agardio.manager Slave Modbus Specification” Hager Group"]
[]
["Available Blocks:",1]
["Maximum Words per Block:",64]